## Slide 1: LOCAFI+
Temperature assessment of a vertical member subjected to LOCAlised FIre
Dissemination
Grant Agreement n° 754072
3. Experimental tests and CFD calibration

## Slide 2: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
Characterisation of heat fluxes received by elements engulfed into the fire
24 tests have been performed by the University of Liège varying:
  The diameter of the fire (5 diameters : 0.6m, 1.0m, 1.4m, 1.8m and 2.2m)
  The type of combustible (2 different combustible liquids (diesel and N-heptane) + 1 cellulosic fire load)
  The presence of a column engulfed into the fire
For each diameter and for the two combustible liquids:
  One test without column into the fire
  One test with a column at the centre of the fire source

## Slide 3: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
General test set-up
Two tanks filled of heptane and diesel were placed at higher height than the floor to allow the fuel to flow by gravity ;
The Rate of Heat Release of the pool fire was controlled by adjusting the flow of injected combustible by a simple manual valve ;
The basin was continuously fed with cold water in order to cool down the layer underneath the burning fuel and, thus to provide a more stable steady burning regime by avoiding water ebullition.

## Slide 4: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
Experimental measurements : flame length
The mean flame length L is the distance above the fire source where the intermittency has declined to 0.5, where intermittency I(z) is defined as the fraction of time the flame lies above the fire source. This assessment was made using digital image analysis.
The difference between the experimental flame length and the flame length predicted by Heskestad is between +30% and -30% but this is in line with other pool fire investigations and mainly due to uncertainty about combustion efficiency and fuel density.
N. Tondini, J.M. Franssen, “Analysis of experimental hydrocarbon localised fires with and without engulfed steel members”, Fire Safety Journal 92 (2017), 9-22

## Slide 5: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
Tests are performed until reached a steady-state configuration (measurements of gas temperature and radiative heat flux are stabilised) ;
In configuration with steel columns, thermocouples also provide evolution of steel temperature.
Experimental measurements : temperature and fluxes
Stable interval

## Slide 6: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
Experimental measurements : temperature and fluxes
(fuel : heptane)
(fuel : diesel)
Heskestad correlation (EN 1991-1-2) over-estimates temperatures both in the flame (qg > 500°C) and the plume (qg < 500°C)

## Slide 7: Tests performed at the University of Liège
3. Experimental tests and CFD calibration
Experimental measurements : temperature and fluxes
EN 1991-1-2 correlation provides a good assessment of temperatures both in the flame (qg > 500°C) and the plume (qg < 500°C).
500

## Slide 8: Tests performed at the University of Ulster
3. Experimental tests and CFD calibration
Characterisation of heat fluxes received by elements outside the fire
58 tests have been performed by the University of Ulster varying:
  The presence or not of a ceiling (37 tests without / 21 tests with)
  The number of pool fires (from 1 to 4) and diameter of these pools (2 diameters : 0.7m and 1.6m)
  The type of combustible (2 different combustible liquids (diesel and kerosene) + 1 cellulosic fire load)
The 9mx9m structure is composed of three types of columns (I-section, H-section and O-section)
The HRR varied with time (not controlled) and was measured by a calorimeter hood
Flame length is assessed using a camera and on the basis of the flame presence probability

## Slide 9: Tests performed at the University of Ulster
3. Experimental tests and CFD calibration
Height | Tests O8, I9 (Kerosene, D1.6m) |  | Test O10 (Diesel, D1.6m) |  | Tests O1,O2 (Kerosene, D0.7m) |  | Tests O3,O4 (Diesel, D0.7m) |  | Test O14 (Wood cribs) | 
 | EN | tEST | EN | tEST | EN | tEST | EN | tEST | EN | tEST
1M | 900 | 949 | 900 | 899 | 900 | 686 | 900 | 652 | 900 | 527
2m | 900 | 810 | 900 | 660 | 845 | 223 | 697 | 208 | 900 | 440
3m | 900 | 515 | 900 | 339 | 381 | 90 | 325 | 89 | 640 | 317
4m | 730 | 312 | 663 | 235 | 228 | - | 198 | - | 391 | 185
5m | 479 | 179 | 440 | 146 | 157 | - | 139 | - | 271 | 159
These tests confirm that Heskestad correlation (EN 1991-1-2) over-estimates temperatures in the flame (qg > 500°C) and the plume (qg < 500°C) domains.
Experimental measurements : flame temperature

## Slide 10: Tests performed at the University of Ulster
3. Experimental tests and CFD calibration
Experimental measurements : temperature and fluxes outside the fire
Plate
Thermometer (TP)
Thermocouples
(TC)
Flux gauges

## Slide 11: Tests performed at the University of Ulster
3. Experimental tests and CFD calibration
Experimental measurements : results obtained from O8 test
Number of Pan(s) : 1
Diameter of the pan : 1.6 m
Fuel type : Kerosene
Fuel quantity : 60 L
Pool-column distance : 0 m
Gauges-column distance : 1.5m
No ceiling

## Slide 12: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Objectives
The number of tests is limited and the measurements made during these tests are limited too.
Due to the dimensions of the building/lab where the experimental tests have been undertaken, it was not possible to cover the full range of localised fires (Annex C of EN 1991-1-2 applies until D = 10 m and Q = 50 MW)
 After validation of the model(s), CFD modelling is a cost-effective and powerful tool able to provide a very large set of results for further validation of analytical calculation methods
FDS software is a free software, developed by NIST, and widely-used by the community of fire engineers
Calibration of FDS models was processes by reproducing a selection of 5 tests chosen on the basis of the following criteria
Tests performed under constant and controlled conditions (Liège) and free conditions (Ulster)
Tests exhibiting long stable and steady-state results
Different types of fuels, small and large pool diameters, with and without ceiling,…

## Slide 13: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Calibration parameters
The most influencing parameters adjusted during the calibration process are :
Turbulence model (Smagorinski, Cs = 0.1)
Fuel properties, including soot yield, taken from literature (overventilated conditions)
Number of Radiation Angles (200)
Radiative loss fraction (range of 0.2-0.5, mainly depending on fuel type and fire diameter)
Wind effects (based on measurements)
Mesh grid dimensions (based on characteristic length and measure of turbulence resolution)
Example of flux variations due to an insufficient number of Radiation Angles

## Slide 14: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Test ULG 06 (D = 1m, Heptane, no column)
Average fuel flow qfuel | 0.98 l/min
Fuel density ρ | 675 kg/m3
Soot yield ysoot | 0.037
Ideal heat of combustion ∆Hc,ideal | 44600 kJ/kg
Heat of combustion ∆Hc | 41200 kJ/kg
RHR computed with ∆Hc,ideal | 491.7 kW (626.1 kW/m2)
Dimension of the CFD domain : 5.75m x 3m x 4m
Grid size : 5cm x 5 cm x 5 cm
Wind speed : 0.22 m/s
Radiative loss fraction : 0.45 (SFPE)

## Slide 15: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Test ULG 06 (D = 1m, Heptane, no column)

## Slide 16: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Test Ulster O29 (D = 0.7m, Diesel, with ceiling at 3.5m)
Fuel density ρ | 823 kg/m3
Soot yield ysoot | 0.10
Ideal heat of combustion ∆Hc,ideal | 44000 kJ/kg
Heat of combustion ∆Hc | 41200 kJ/kg
RHR computed with ∆Hc,ideal | 491.5 kW (1277.1 kW/m2)
Dimension of the CFD domain : 7m x 7m x 3.5m
Grid size : 5cm x 5 cm x 5 cm
Wind speed : 0.76 m/s
Radiative loss fraction : 0.45 (SFPE)

## Slide 17: Calibration of a CFD model using FDS software
3. Experimental tests and CFD calibration
Test Ulster O29 (D = 0.7m, Diesel, with ceiling at 3.5m)
z (m) | CFD RHFG GG (kW/m2) | EXP GG (kW/m2) | Error (%)
1 | 17.35 | 15.45 | 12.3
2 | 4.71 | 5.32 | -11.5

## Slide 18: French tests (not in the scope of LOCAFI+)
3. Experimental tests and CFD calibration
Tests initiated by LCPP in a large volume :
Main hall : 300 m x 50 x 17 m
2 kinds of combustibles : wood pallet / kerosen
Fire tests repeated
Highly instrumented : thermocouples, gauge heat flux, videos (IR and normal)

## Slide 19
3. Experimental tests and CFD calibration
Ethanol pool
Small
Medium
Huge
Small test : ~ 20 palets
Medium test : ~ 60 palets
Huge test : ~ 110 palets

## Slide 20
3. Experimental tests and CFD calibration
HRR ~ 30 MW