## Slide 1: LOCAFI+
Temperature assessment of a vertical member subjected to LOCAlised FIre
Dissemination
Grant Agreement n° 754072
2. State-of-the-art and reason for the project

## Slide 2: State-of-the-art : Development of a fire
2. State-of-the-art and reason for the project
Flame
(Activation energy)
Oxygen
(Combustive)
Wood, Plastic, Gas…
(Fuel)
Starting of a fire :
Presence of 3 things simultaneously
End of a fire :
Oxygen and/or Fuel missing

## Slide 3: State-of-the-art : Development of a fire
2. State-of-the-art and reason for the project
Step 1 : Fire ignition (localised fire, action of firemen/sprinkler possible)
Step 2 : Development of the fire (depending on ventilation, fire load,…)
Between 2 and 3 : Flashover (from local to general)
Step 3 : Fully-developped fire
Step 4 : Decay phase (reduction of RHR due to missing fuel)

## Slide 4: State-of-the-art : Prescriptive fire curve
2. State-of-the-art and reason for the project
0
200
400
600
800
1000
1200
0
30
60
qg
[°C]
90
120
180
Time [min]
ISO
ISO
ISO
ISO
ISO
ISO
ISO
ISO
Has to be considered in the WHOLE compartment, even if the compartment is huge
Never goes DOWN
Does not consider the PRE-FLASHOVER PHASE
Does not depend on FIRE LOAD and VENTILATION CONDITIONS
1110
945
1006
1049
842
qg = 20 + 345 log (8 t + 1)
ISO-834 Curve (EN1364 -1)

## Slide 5: State-of-the-art : Performance-based fire
2. State-of-the-art and reason for the project
LOCALISED FIRE
LOCALISED FIRE
FULLY ENGULFED
COMPARTMENT
The Fire stays localised
The Fire switch to a
fully engulfed fire
No flashover
occurs
Flashover
occurs

## Slide 6: State-of-the-art : Performance-based fire curve
2. State-of-the-art and reason for the project
Temperature
Cooling ….
ISO834 standard fire curve
Ignition - Smouldering
Pre- Flashover
Heating
Post- Flashover
Natural fire curve
Time
Boundary properties
Ceiling height
Opening Area
Fire surface
Rate of heat release
Geometry
Fire
Influencing parameters
Flashover

## Slide 7: State-of-the-art : Performance-based fire curve
2. State-of-the-art and reason for the project
Step 1 : Division of the building into compartments
Occupancy
Fire Growth
Rate
RHR
f
[kW/m²]
Fire Load
q
f,k
80%
fractile
[MJ/m²]
Dwelling
Medium
250
948
Hospital
(room)
Medium
250
280
Hotel
(room)
Medium
250
377
Library
Fast
500
1824
Office
Medium
250
511
School
Medium
250
347
Shopping Centre
Fast
250
730
Theatre
(movie/cinema)
Fast
500
365
Transport
(public space)
Slow
250
122
Step 2 : Physical parameters linked to Occupancy

## Slide 8: State-of-the-art : Performance-based fire curve
2. State-of-the-art and reason for the project
Step 3 : Danger of Fire Activation
Step 4 : Active measures
Compartment floor area Af [m2] | Danger of Fire Activation dq1 | Examples of Occupancies | Danger of Fire Activation dq2
25 | 1.10 | Art gallery, museum, swimming pool | 0.78
250 | 1.50 | Residence, hotel, office | 1.00
2500 | 1.90 | Manufactory for machinery & engines | 1.22
5000 | 2.00 | Chemical lab, painting workshop | 1.44
10000 | 2.13 | Manufactory of fireworks or paints | 1.66
Sprinkler | Independent Water Suppl. 0 ¦ 1 ¦ 2 | Fire Detection Heat ¦ Smoke | Alarm Transm. | Work Brigade | Off Site Brigade | Safe Road Access | Fire Fighting Devices | Smoke Exhaust System
0.61 | 1.0 ¦ 0.87 ¦ 0.7 | 0.87 ¦ 0.73 | 0.87 | 0.61 | 0.78 | 0.9 ¦ 1.0 ¦1.5 | 1.0 ¦ 1.5 | 1.0 ¦ 1.5

## Slide 9: State-of-the-art : Performance-based fire curve
2. State-of-the-art and reason for the project
Step 5 : Design fire load
Step 6 : RHR diagram

## Slide 10: State-of-the-art : Localised fire
2. State-of-the-art and reason for the project
In some circumstances, the analysis of the structure under natural fire is not sufficient/realistic :
Very large (or complex) compartment
Ventilation controlled fire
Fire load is localised (car park)
qg (t) uniform in the compartment
qg (x, y, z, t)

## Slide 11: State-of-the-art : Localised fire
2. State-of-the-art and reason for the project
Currently two models are available in the EN1991-1-2 Annex C to describe the effects of localised fire to the structure:
For car parks structures, several experimental campaigns have been used to validate the Hasemi model as design tool able to reproduce with sufficient safety margin the temperature field in horizontal structural elements caused by burning cars.
Heskestad model
for fire not impacting the ceiling
Hasemi model
for fire impacting the ceiling

## Slide 12: Reason for the project
2. State-of-the-art and reason for the project
Y
Annex C of EN 1991-1-2:
Flame impacting the ceiling
Annex C of EN 1991-1-2:
Flame not impacting the ceiling
In this situation, column temperature is mainly governed by radiative fluxes. But how to tackle this ?
Flame axis
L
z
D
f
H
Y = Height of the free zone
concrete slab
q
g
beam

## Slide 13: Objectives of LOCAFI Project
2. State-of-the-art and reason for the project
Providing scientific evidence about the thermal attack imposed on a steel column surrounded by a local fire or attacked by a local fire at a distance from the column (including verification of equations providing temperature along centreline of the source) ;
Providing design equations that allow reproducing this thermal attack as well as temperatures induced in the column, publication of these equations and implementation in existing software (OZone, SAFIR,…) ;
Providing rules that form the basis of the design equations in order to have them implemented in Eurocodes, which will make the models automatically accepted without any discussion by the authorities of the different Member States.