## Slide 1: LOCAFI+
Temperature assessment of a vertical member subjected to LOCAlised FIre
Dissemination
Grant Agreement n° 754072
4. Analytical method and validation

## Slide 2: 4.1. Concept of Virtual Solid Flame
4. Analytical method and validation
Modelling of the flame
  Step 1: The surface of the fire is transformed into an equivalent discus
  Step 2: The evolution of Heat Release Rate is calculated according to EN 1991-1-2 Annex E (growing phase, plateau, decaying phase)
  Step 3: The flame length Lf is calculated by application of EN 1991-1-2 Annex C
  Step 4: The action of the fire is represented by a virtual solid flame, conic or cylindric, defined by Deq and Lf
HRRmax (fuel or ventilation controlled)
parabolic
constant
linear
time
Q (or HRR)
Deq
Deq
Lf
Cone model
Cylinder model

## Slide 3: 4.1. Concept of Virtual Solid Flame
4. Analytical method and validation
Modelling of the flame
Deq
Deq
Lf
Cone model
Cylinder model
  If the flame does not impact the ceiling (Lf < Hceiling or no ceiling)
θf (z)
Lf
z
θf (z)
z

## Slide 4: 4.1. Concept of Virtual Solid Flame
4. Analytical method and validation
Modelling of the flame
Deq
Hceiling
Cone model
Cylinder model
  If the flame does impact the ceiling (Lf > Hceiling)
z
Deq
Lh
r
θf (r)
θf (z)
z
Lh
r
θf (r)
θf (z)

## Slide 5: 4.2. Geometrical method for exchanged heat fluxes
4. Analytical method and validation
Assessment of radiative heat fluxes
  the emissivity e1 (of the emitting surface) is assumed equal to 1 for flames
  the absorptivity a2 depends on the receiving surface properties
  Kirchoff Law : absorptivity (a) = emissivity (e)
  For steel, e = a = 0.7
  The radiative heat flux leaving a given radiating surface dA1 and received by a surface dA2 is :
  Impinging radiative flux
  Absorbed flux
  Reflected flux

## Slide 6: 4.2. Geometrical method for exchanged heat fluxes
4. Analytical method and validation
  Concave sections imply shadow effect  As a simplification, heat fluxes are calculated on a convex perimeter
  For I- or H-sections, the structural member is transformed into a rectangular-shape tubular section (in line with EN 1991-1-2 Annex G)
  Then, the perimeter surface is sub-divided into faces
Equivalent rectangular envelope
Model of the vertical member
Section
3D view
Facei
Modelling of the vertical member

## Slide 7: 4.2. Geometrical method for exchanged heat fluxes
4. Analytical method and validation
Numerical integration
  Each “individual” radiative exchange is calculated (at each time step).
  Requires a program for real applications.
  Allows applying non-uniform conditions (radiative fluxes) on the section perimeter.

## Slide 8: 4.3. Simplified model
4. Analytical method and validation
Factor view between an infinitesimal surface and a cylinder
dA1
h
y
x
s
A2
r
  Valid only if the plane defined by dA1 does not intersect the cylinder !

## Slide 9: 4.3. Simplified model
4. Analytical method and validation
Factor view between an infinitesimal surface and a ring
  Valid only if l > r2 !
dA1
A2
r2
r1
h
l

## Slide 10: 4.3. Simplified model
4. Analytical method and validation
Sub-division of the flame into cylinders and rings
  If the flame does impact the ceiling
  (Lf > Hceiling)
  If the flame does not impact the ceiling
  (Lf < Hceiling or no ceiling)
  Note : the contribution of the ring is really low, except if the member is situated in the ring

## Slide 11: 4.3. Simplified model
4. Analytical method and validation
Sub-division of the flame into cylinders and rings (Adaptation 1)
Truncated cones
Cylinders and rings
Conical solid flame
! By neglecting the contribution of rings, we underestimate the received flux and could even obtain a received flux equal to 0 above the fire !

## Slide 12: 4.3. Simplified model
4. Analytical method and validation
Sub-division of the flame into cylinders and rings (Adaptation 2)
Face 2
Face 4
Face 3
Face 1
Intersection
Intersection
No intersection
! The formula for cylinder is not valid if the receiving surface intersect the cylinder !

## Slide 13: 4.3. Simplified model
4. Analytical method and validation
Sub-division of the flame into cylinders and rings (Adaptation 2)
In this case, initial cylinder transformed into a modified cylinder in the visible zone
visible
Modelling
Face 4
not visible
Modified cylinder
Top view
3D view

## Slide 14: 4.3. Simplified model
4. Analytical method and validation
Sub-division of the flame into cylinders and rings (Adaptation 3)
rzi
rzi+1_adjusted
rzi+1
rzi_adjusted
Top view
3D view
A portion of rings is « hidden » by the cylinder situated above  A reduced zone should be considered
(safe-sided to ignore this reduction…)

## Slide 15: 4.3. Simplified model
4. Analytical method and validation
Additional remarks
  Recommended width of cylinder is 50 cm
  For elements situated below the ceiling, convection should be added  Hasemi
  For several fires, the fluxes received from each fire must be added. The total received flux is limited to 100 kW/m2
  The member temperature is calculated by stating the thermal balance of the member
[W.m-2]
ρ, Cp, and Am/V are density [kg.m-3], specific heat [J.kg-1.K-1] and massivity [m-1] of the member
[W.m-2]

## Slide 16: 4.3. Simplified model
4. Analytical method and validation
Model validation based on Liège tests (and FDS modelling)
Diam. | Experiment mean value | Tests no | Cylinder flame | Conic flame
[m] | [kW/m²] | [-] | [kW/m²] | [kW/m²]
0.60 | 0.31 | 1 to 4 | 1.20 | 0.74
1.00 | 0.73 | 5 to 8 | 3.23 | 1.95
1.40 | 1.36 | 9 to 14 | 6.19 | 3.67
1.80 | 2.12 | 15 to 18 | 9.95 | 5.78
2.20 | 3.39 | 19 to 22 | 14.55 | 8.30
  Gauge situated at 3.75 m from the fire source (height : 1.75 m)
  Orientation of the gauge : perpendicular to the fire-gauge axis

## Slide 17: 4.3. Simplified model
4. Analytical method and validation
Model validation based on Ulster tests (and FDS modelling)
Gauge
TC

## Slide 18: 4.3. Simplified model
4. Analytical method and validation
Model validation based on Ulster tests (and FDS modelling)
Case 1a
1 pan
D = 0.7 m
Gauges at 0.5/1.8 m
Case 1b
1 pan
D = 0.7 m
Gauges at 1.0/1.6 m
Gauge location |  | Experiment mean | FDS Simulation | Cylinder flame | Conic flame
Height | Distance |  |  |  | 
m | m | kW/m² | kW/m² | kW/m² | kW/m²
1.0 | 0.5 | 30.6 | 28.5 | 74.0 | 39.0
1.0 | 1.0 | 13.8 | 12.9 | 33.2 | 17.9
1.0 | 1.6 | 5.9 | 5.5 | 15.5 | 8.5
1.0 | 1.8 | 4.2 | 3.8 | 10.8 | 6.0
2.0 | 0.5 | 6.2 | 11.2 | 22.0 | 5.9
2.0 | 1.0 | 4.5 | 5.9 | 14.1 | 5.5
2.0 | 1.6 | 3.0 | 3.7 | 8.8 | 4.1
2.0 | 1.8 | 2.3 | 2.6 | 6.7 | 3.3

## Slide 19: 4.3. Simplified model
4. Analytical method and validation
Model validation based on Ulster tests (and FDS modelling)
Case 3
3 pans
D = 0.7 m
Gauges at 1.0 m
Case 5
1 pan
D = 1.6 m
Gauges at 1.5 m
Gauge location |  | Experiment mean | Simulation mean | Cylinder flame | Conic flame
Height | Distance |  |  |  | 
m | m | kW/m² | kW/m² | kW/m² | kW/m²
1.0 | 1.0 | 31.0 | 26.6 | 66.3 | 37.4
1.0 | 1.0 | 24.3 | 21.6 | 62.0 | 34.6
2.0 | 1.0 | 15.0 | 17.7 | 40.9 | 16.2
2.0 | 1.0 | 13.0 | 13.6 | 38.5 | 15.9
Gauge location |  | Experiment mean | Simulation mean | Cylinder flame | Conic flame
Height | Distance |  |  |  | 
m | m | kW/m² | kW/m² | kW/m² | kW/m²
1.0 | 1.5 | 37.6 | 33.6 | 53.9 | 38.9
2.0 | 1.5 | 26.5 | 24.5 | 55.2 | 29.7

## Slide 20: 4.3. Simplified model
4. Analytical method and validation
Model validation for large diameters (LCPP tests)

## Slide 21: 4.4. Contour plots
4. Analytical method and validation
Provide a new set of results for validation of SAFIR and OZone implementations
Provide quick and safe results for a wide range of configurations (predesign) and an interpolation method to apply it to a much wider range of configurations
Provide a set of reference results for validation of implementation of analytical methods by practitioners (spreadsheets or software)
D = 2m, RHR = 500 kW/m2, q = 0° (left) or q = 90° (right)

## Slide 22: 4.4. Contour plots
Each nomogram is characterised by :
the diameter of the fire (m)
the RHR (kW/m2)
the orientation of the receiving surface (°)
Nomograms only account for radiation. Not used :
Inside the fire  HESKESTAD
At the ceiling level  HASEMI
Assumes that the flame emissivity is 1.0
D
n1
O
n2
Finite Surface 1 : q = 0°
Finite Surface 2 : q = 90°
4. Analytical method and validation

## Slide 23: 4.4. Contour plots
Case | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
D (m) | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4
HRR (kW/m²) | 250 | 500 | 1000 | 1500 | 250 | 500 | 1000 | 1500 | 250 | 500 | 1000 | 1500
Power (MW) | 0.8 | 1.6 | 3.1 | 4.7 | 1.8 | 3.5 | 7.1 | 10.6 | 3.1 | 6.3 | 12.6 | 18.8
Case | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
D (m) | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 9 | 9 | 9 | 10 | 10
HRR (kW/m²) | 250 | 500 | 1000 | 1500 | 250 | 500 | 1000 | 250 | 500 | 750 | 250 | 500
Power (MW) | 7.1 | 14.1 | 28.3 | 42.4 | 12.6 | 25.1 | 50.3 | 47.7 | 15.9 | 31.8 | 19.6 | 39.3
Scope of application of the method (idem Annex C of EN 1991-1-2) : D < 10 m ; Q < 50 MW
 The chosen configurations cover the field of application of the calculation method
4. Analytical method and validation

## Slide 24: 4.4. Contour plots
4. Analytical method and validation
Localised fire characteristics :
D = 10 m
RHR : 500 kW/m2
Target position
Z = 5m
X = 10 m
Orientation : 0°
Received Flux = 16 kW/m2
Target position
Z = 5m
X = 10 m
Orientation : 90°
Received Flux = 2.4 kW/m2

## Slide 25: 4.5. Conclusions
4. Analytical method and validation
  LOCAFI project introduces the new concept of Virtual Solid Flame.
  The distribution of temperature on the perimeter of the Virtual Solid Flame is based on existing equations of EN 1991-1-2 Annex C (Heskestad, Hasemi).
  The exchange of radiative fluxes is based on the configuration factor of EN 1991-1-2 Annex G.
  The simplified model is based on mathematical equations providing the radiative flux received by an infinitesimal surface from cylinders and rings.
  The convective fluxes must be calculated separately. However, convective heat fluxes have a significant effect only in configurations already covered by EN 1991-1-2 Annex C (members engulfed into fire or situated at the ceiling level).