## Slide 1: LOCAFI+
Temperature assessment of a vertical member subjected to LOCAlised FIre
Dissemination
Grant Agreement n° 754072
6. Synthesis Fire resistance

## Slide 2: 6.1. General Procedure
6. Synthesis Fire resistance
Step 1 : Definition of thermal loading
Step 2 : Thermal Analysis
Step 3 : Mechanical Analysis
The general procedure is step-by-step (Step 1  Step 2  Step 3) but, more accurately, the coupling should be in both directions. If this double coupling is not considered, the engineer must be aware of the associated assumptions !
The deflections/displacements of a structural element may influence the development of the fire
The deflections/displacements of a structural element may influence the thermal exposure
The elevation of temperature in members may influence the absorbed energy absorbed in walls/floors
Plasticity and cracking may induce generation of heat or heat leakage
…

## Slide 3: 6.2. Definition of fire scenario
6. Synthesis Fire resistance
6.2.1. Compartment fire
Standard fire curve (ISO-834, Hydrocarbon,…)
Natural fire curve (parametric curve according to Annex A of EN 1991-1-2, OZone software based on EN 1991-1-2 Annexes D and E)
6.2.2. Localised fire
Fire scenario defined by engineer/authorities (diameter, RHR)

## Slide 4: 6.2. Definition of fire scenario
6. Synthesis Fire resistance
6.2.2. Localised fire
(1) : Heskestad
(2) : Hasemi
(3) : LOCAFI
(radiation)

## Slide 5: 6.3. Thermal analysis
6. Synthesis Fire resistance
6.3.1. Steady-state temperature
  Steady-state temperature q is the temperature at which the received flux is equilibrated by the emitted (convective and radiative) fluxes
  Emitted net convective flux
  Emitted radiative flux
  Received flux
  In case of compartment fire, the mean impinging radiative flux must be replaced by including both convective and radiative fluxes.
  This simplified approach neglects the thermal inertia of the member
[W.m-2]
[W.m-2]

## Slide 6: 6.3. Thermal analysis
6. Synthesis Fire resistance
6.3.2. Incremental procedure (uniform temperature)
  The member temperature is calculated by stating the thermal balance of the member
ρ, Cp, and Am/V are density [kg.m-3], specific heat [J.kg-1.K-1] and massivity [m-1] of the member
  EN 1993-1-2 imposes that the time step Dt is not higher than 5 seconds
  In case of compartment fire, the mean impinging radiative flux must be replaced by including both convective and radiative fluxes.
[W.m-2]

## Slide 7: 6.3. Thermal analysis
6. Synthesis Fire resistance
6.3.2. Incremental procedure (uniform temperature)
Specific Heat (J/kg°K)
5000
0
200
400
600
800
1000
1200
Temperature (°C)
4000
3000
2000
1000
Volumic mass of steel : 7850 kg/m3
Independent of temperature

## Slide 8: 6.3. Thermal analysis
6. Synthesis Fire resistance
6.3.3. F.E. thermal analysis (non-uniform temperature)
Temperature distribution [°C] after 33 minutes for a 3.36 [m] column with a 130[mm]x130[mm] square cross section surrounded by 3 cars and 1 van at a) a height of 0.94[m] ; b) a height of 3.1[m]

## Slide 9: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. General rules of EN 1993-1-2
Only load bearing function R of steel structures is covered by the design rules of the fire part of Eurocode 3
Load bearing function of a structure is satisfied only if during the relevant duration of fire exposure t
Efi,d,t  Rfi,d,t
where Efi,d,t : design effect of actions (Eurocodes 0 and 1)
Rfi,d,t : corresponding design resistance of the structure at instant t

## Slide 10: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. General rules of EN 1993-1-2
1.35*Gk,j + 1.5*Qk,1 + 1.5* 0,i Qk,i
j  1
i  2
Ed =
Recommended, for practical application refer to each National Annex
Actions | Y0 | Y1 | Y2
Category A : domestic, residential areas | 0.7 | 0.5 | 0.3
Category B : office areas | 0.7 | 0.5 | 0.3
Category C : congregation areas | 0.7 | 0.7 | 0.6
Category D : shopping area | 0.7 | 0.7 | 0.6
Category E : storage areas | 1 | 0.9 | 0.8
… | … | … | …
Gk,j + 2,1 Qk,1 +  2,i Qk,i
j  1
i  2
Efi,d,t =
ULS Combination
ACC Combination

## Slide 11: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. General rules of EN 1993-1-2
Partial factors of steel at elevated temperatures
Type of members | Cold design | Fire design
Cross-sections | M0 = 1.0 | M,fi = 1.0
Members with instability | M1 = 1.0 | M,fi = 1.0
Tension members to fracture | M2 = 1.25 | M,fi = 1.0
Joints | M2 = 1.25 | M,fi = 1.0

## Slide 12: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. General rules of EN 1993-1-2
Bracing system
Lfi=0.7L2
Lfi=0.5L1
L2
L1
Conditions :
  Braced structures
  Continued or ends maintained columns
  Same fire resistance R between columns and floor members

## Slide 13: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. General rules of EN 1993-1-2
Verification of fire resistance according one of the 3 following methods :
Temperature : qcr,d ≥ qd
Load resistance : Rfi,d,t ≥ Efi,d,t
Time : tfi,d ≥ tfi,required
Most simple and commonly-used method, only valid for uniform T°
Feasible by hand calculation (reduced capacity at required time)
Only feasible using advanced tools, like Finite Element Models

## Slide 14: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.2. Analytical verification of column according to EN 1993-1-2
Current version of EN 1993-1-2 applies to steel grades S235 to S460
Temperature (°C)
Reduction factor (-)
ky,q : reduction of yield limit
kE,q : reduction of Young modulus
kp,q : reduction of proportional limit
Temperature

## Slide 15: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.2. Analytical verification of column according to EN 1993-1-2
Gk,j + 2,1 Qk,1 +  2,i Qk,i
j  1
i  2
Efi,d,t =
Recommended, for practical application refer to each National Annex
Accidental combination loading
Reduction factor for the level of loading
Temperature
1.35*Gk,j + 1.5*Qk,1 + 1.5* 0,i Qk,i
j  1
i  2
Ed =

## Slide 16: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. Analytical verification of column according to EN 1993-1-2
Reduction factor for the level of loading
In structural fire design ACC design
gGA = 1.0 Permanent loads;
y2.1 = 0.3 Combination factor; variable loads, offices
Ambient temperature ELU design
gG = 1.35 Permanent loads;
gQ.1 = 1.50 Combination factor; variable loads
Temperature
EN 1993-1-2 recommends hfi = 0.65 (except Category E, hfi = 0.7)

## Slide 17: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.2. Analytical verification of column according to EN 1993-1-2
Gk,j + 2,1 Qk,1 +  2,i Qk,i
j  1
i  2
Efi,d,t =
Recommended, for practical application refer to each National Annex
Accidental combination loading
Reduction factor for the level of loading
Temperature
Ambient temperature design resistance

## Slide 18: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. Analytical verification of column according to EN 1993-1-2
Temperature
Accounts for partial safety factors at room and elevated T° (normally both of them are 1.0)
Allows a direct calculation of the critical T°
In case the failure mode includes instabilities, the reduced non-dimensional slenderness is required
Degree of Utilisation

## Slide 19: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. Analytical verification of column according to EN 1993-1-2
Temperature
0.0
0.2
0.4
0.6
0.8
1.0
1.2
1.4
1.6
1.8
2.0
0
0.04
1000
977
949
913
880
839
787
742
696
678
659
0.06
900
885
866
837
795
756
700
679
656
630
602
0.08
860
839
811
785
749
697
674
647
616
588
564
0.10
820
797
780
752
703
677
648
614
585
557
527
0.12
792
777
755
719
685
656
622
588
559
526
474
0.14
775
757
730
694
668
636
597
567
533
487
373
0.16
758
737
705
681
652
615
580
546
507
408
0.18
742
717
691
668
636
596
563
524
453
0.20
725
698
680
655
619
582
545
503
384
0.22
708
689
669
641
603
568
528
457
0.24
696
679
658
628
591
554
511
406
0.26
688
670
647
615
579
540
485
0.28
679
660
636
602
568
526
446
…
…
…
…
…
…
…
…
Critical temperature of steel members under instability using specific tabulated data based on:
  non-dimensional slenderness at instant 0
  and a specific load level 0 = Nfi,d,t / Npl,fi,0
  each steel grade has its own tabulated data

## Slide 20: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.2. Analytical verification of column according to EN 1993-1-2
Current version of EN 1993-1-2 applies to steel grades S235 to S460
Temperature (°C)
Reduction factor (-)
ky,q : reduction of yield limit
kE,q : reduction of Young modulus
kp,q : reduction of proportional limit
Load resistance

## Slide 21: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.1. Analytical verification of column according to EN 1993-1-2
Load resistance
Lfi
Nfi,d,t
Section and temperature
0
0.5
1.0
l
Specific buckling curve
()

## Slide 22: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.2. Analytical verification of column according to EN 1993-1-2
Gk,j + 2,1 Qk,1 +  2,i Qk,i
j  1
i  2
Efi,d,t =
Recommended, for practical application refer to each National Annex
Accidental combination loading
Design criteria
Load resistance
Rfi,d,t ≥ Efi,d,t

## Slide 23: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.3. Finite element analysis
Normalised stress
Strain (%)
20°C
200°C
400°C
500°C
600°C
700°C
800°C
0
0.2
0.4
0.6
0.8
1
0
5
10
15
20
2
Stress-strain diagram of steel is non-linear (elastic, parabolic, plateau, descending branch)
Yield strength at 600°C reduced by over 50%
Time

## Slide 24: 6.4. Mechanical analysis
6. Synthesis Fire resistance
0
5
10
15
20
0
200
400
600
800
1000
1200
Temperature (°C)
L/L (x103)
6.4.3. Finite element analysis
Thermal expansion of steel
Time

## Slide 25: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.3. Finite element analysis
Nb,Rd,cold
Loss of equilibrium
Cold design
- Initial imperfection
- Load increases until failure
NEd,ACC
Loss of equilibrium
Hot design
- Initial imperfection
- Initial loading
- Temperature increases until failure

## Slide 26: 6.4. Mechanical analysis
6. Synthesis Fire resistance
6.4.3. Finite element analysis
Time
Left : Temperature distribution at Node 1068 after 33 minutes along a 3.36 [m] column with a 130[mm]x130[mm] square cross section surrounded by 3 cars and 1 van
Right : Displacement shape in failure (scale factor 1) of a 3.36[m] column with a 130[mm]x130[mm] square cross section surrounded by 3 cars and 1 van