## Slide 1: LOCAFI+
Temperature assessment of a vertical member subjected to LOCAlised FIre
Dissemination
Grant Agreement n° 754072
7. Worked examples

## Slide 2: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Column section : HEB 300
Diameter of the fire source : 4m
Distance between the fire and the column : 0.5m
Rate of heat release : 1000 kW.m-2
Conic flame
Column situated outside the fire and the smoke layer
No ceiling
Calculation is made for z = 1.0m

## Slide 3: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
= 6.15 m
Flame temperature
= -0.48 m
z (m) | T (°C)
0 | 900
0.5 | 900
1 | 900
1.5 | 900
2 | 900
2.5 | 900
3 | 900
3.5 | 900
4 | 900
4.5 | 827.9
5 | 708.4
5.5 | 614.8
6 | 540.0
6.5 | 479.3
7 | 429.1
7.5 | 387.2
θf (z)
Lf
z

## Slide 4: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
dA1
h
y
x
s
A2
r
Face 1

## Slide 5: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
zf = 1.0m
Only one ring to consider (zi = 0.5m)
External radius r2 = 2.0m
Internal radius r1 = (6.15-0.5)/6.15*2.0m = 1.84m
Simplification : l = 2.5m
= = 0.2
= = 0.8
= = 0.73
Face 1

## Slide 6: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Face 1

## Slide 7: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Face 1
= 0.7*77 kW/m2
= 53.9 kW/m2

## Slide 8: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Face 2
Modelling
Face 2
Modified cylinder
Top view
= 0
= 2.0 m
= 1.0 m
= 1.0 m
z = 0

## Slide 9: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Face 2

## Slide 10: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Face 2
= 0.7*8.7 kW/m2
= 6.1 kW/m2

## Slide 11: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Heat flux received by each face (assuming e = 0.7)
Face 1 : 53.45 kW/m2
Face 2 : 6.00 kW/m2
Face 3 : 0.00 kW/m2
Face 4 : 6.00 kW/m2
 Mean heat flux = 16.36 kW/m2
  Emitted net convective flux
  Emitted radiative flux
  Received flux
T | Emitted flux
(°C) | W/m2
20 | 0
30 | 392.03
40 | 788.42
50 | 1189.49
… | …
280 | 12519.26
290 | 13145.11
300 | 13786.06
310 | 14442.65
320 | 15115.43
330 | 15804.96
340 | 16511.80
350 | 17236.55
360 | 17979.78

## Slide 12: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples

## Slide 13: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples

## Slide 14: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples

## Slide 15: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Square 300x300
Tube 300x300x10
HEB 300
(Tmax + Tmin)/2 = 306°C
(Tmax + Tmin)/2 = 317°C
Large variation across section
(Tmax + Tmin)/2 = 262°C
Model accounts for shadow factors
Distribution of temperature at equilibrium (LOCAFI)

## Slide 16: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
  Example 1b
  z = 3.5 m

## Slide 17: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
  Example 1c
  z = 3.5 m
  zceiling = 3.5 m
z
Lh
r
θf (r)
θf (z)
= 4.54 m

## Slide 18: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
= 0.3536
2.4*D* = 1.535
= 0.787
  HASEMI (EN 1991-1-2 – Annex C)

## Slide 19: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples

## Slide 20: 7.1. Example 1 : Radiation fluxes under localised fire
7. Worked examples
Square 300x300
Tube 300x300x10
HEB 300
Taver = 589°C
Taver = 590°C
Taver = 591°C
Distribution of temperature at equilibrium (HASEMI)

## Slide 21: 7.2. Example 2 : Column of an office building
7. Worked examples
Fire source situated at a distance of 0.5 m from the column
Ceiling level : 3.5 m
Fire source : 500 kg of paper (17.5 MJ/kg) on a 2.5m2 area
RHRmax = 1000 kW/m2

## Slide 22: 7.2. Example 2 : Column of an office building
7. Worked examples
Development of the fire according to EN 1991-1-2 Annex E
- Growing phase : Q(t) = 106*(t/ta)2
- Speed of development : Medium
 RHR = 1 MW after ta = 300 sec
- RHRmax = 2.5m2 * 1000kW/m2 = 2.5 MW
- Decay phase starts after 70% of the fuel has burnt

## Slide 23: 7.2. Example 2 : Column of an office building
7. Worked examples
Pos x : 0.5m + 1.8m/2 = 1.4m

## Slide 24: 7.2. Example 2 : Column of an office building
7. Worked examples

## Slide 25: 7.2. Example 2 : Column of an office building
7. Worked examples

## Slide 26: 7.2. Example 2 : Column of an office building
7. Worked examples
Maximum received radiative heat flux in the hot smoke layer
Hot smoke layer (z = 3.5m) : temperature reaches 290°C
Outside smoke layer (z = 0.5m and z = 1m) : ~250°C

## Slide 27: 7.3. Example 3 : Column of a car park
7. Worked examples
HEA 300 column
Ceiling level : 3.5 m
Dimensions of the parking spot : 2.5m*5m
Equivalent diameter of the fire : 4 m
Fire scenario : 3 cars + 1 van (risk analysis – highly severe assumption)
Ignition time between two consecutive cars : 12 minutes

## Slide 28: 7.3. Example 3 : Column of a car park
7. Worked examples
Very severe scenario !

## Slide 29: 7.3. Example 3 : Column of a car park
7. Worked examples

## Slide 30: 7.3. Example 3 : Column of a car park
7. Worked examples
Outside hot smoke layer (z = 1 m) : tmax = 500°C
In hot smoke layer (z = 3.5 m) : tmax = 700°C

## Slide 31: 7.4. Example 4 : Truss of an industrial building
7. Worked examples
Description of the structure :
Truss flanges section : HEA 220
Truss diagonals section : 2 L60*60*6
Distance between 2 steel frames : 10 m
Apex height : 14 m

## Slide 32: 7.4. Example 4 : Truss of an industrial building
7. Worked examples
Fire scenario :
Fire area : 50 m2 (center of storage area)
Equivalent diameter : 8 m
Speed of development : Medium
RHR = 1 MW after ta = 300 sec
RHRmax = 1000 kW/m2*50m2 = 50 MW
Fire Load : 10 To (cellulosic)
 Q = 17.5 MJ/kg*10000 kg = 175000 MJ

## Slide 33: 7.4. Example 4 : Truss of an industrial building
7. Worked examples

## Slide 34: 7.4. Example 4 : Truss of an industrial building
7. Worked examples
Flame height = 9.7m
→ Truss members are situated above the solid flame
Max. temperature of trusses = 210°C

## Slide 35: 7.4. Example 4 : Truss of an industrial building
7. Worked examples

## Slide 36: 7.4. Example 4 : Truss of an industrial building
7. Worked examples
Face 1
= 0.7*15 kW/m2 = 10.5 kW/m2
Face 2
= 0.7*3.5 kW/m2 = 2.45 kW/m2

## Slide 37: 7.4. Example 4 : Truss of an industrial building
7. Worked examples
Heat flux received by each face (assuming e = 0.7)
Face 1 : 10.5 kW/m2
Face 2 : 2.45 kW/m2
Face 3 : 0.00 kW/m2
Face 4 : 2.45 kW/m2
 Mean heat flux = 3.85 kW/m2
  Emitted convective flux
  Emitted radiative flux
  Received flux
T | Emitted flux
(°C) | W/m2
20 | 0
30 | 392.03
40 | 788.42
50 | 1189.49
60 | 1595.53
70 | 2006.84
80 | 2423.77
90 | 2846.62
100 | 3275.76
110 | 3711.52
120 | 4154.27
130 | 4604.37
140 | 5062.21
150 | 5528.18

## Slide 38: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
1
6 m
6 m
6 m
6 m
6 m
A
B
C
7 m
7 m
14 m
2
3
4
5
6
3 m
3 m
3 m
3 m
3 m
3 m
3 m
3 m
S1
S1
S2
S2
S2 - S2
S1 - S1
Bracing system
Bracing system
Bracing system
Bracing system
3 m
3 m

## Slide 39: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Actions (for all floor levels)
Self weight G1:
  composite slab unit weight: 2.12 kN/m²
  steel structural members: according to their sizes
Permanent load G2:
  finishing, services, partitions: 1.50 kN/m²
Permanent load G3:
  Façade cladding load: 2.00 kN/m
Characteristic values of variable loads and  factors
Type | qk | 1 | 2
Live load on floors | 4.0 kN/m² | 0.7 | 0.6
Snow on roof | 1.7 kN/m² | 0.2 | 0.0

## Slide 40: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
1
6 m
6 m
6 m
6 m
6 m
A
B
C
7 m
7 m
14 m
2
3
4
5
6
3 m
3 m
3 m
3 m
3 m
3 m
3 m
3 m
S1
S1
S2
S2
S2 - S2
S1 - S1
Bracing system
Bracing system
Bracing system
Bracing system
3 m
3 m
Structural members
Composite slab:
  Total thickness: 12 cm
  Steel deck: COFRAPLUS60
  Thickness of steel deck: 0.75 mm
  Continuous slab over 2 spans
Common secondary beams:
  IPE360 - S275
Internal main beams:
  HEA360 - S275
Columns for ground level:
  Edge columns (ground level): HEA300 - S275
  Central columns (ground level): HEB300 - S275

## Slide 41: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Studied system
Design load per level
from secondary beam: 98.7 kN
Design load per level
from main beam: 209.2 kN
Self weight of HEB300 = 1.15 kN/m
Design load in fire situation
Design load in fire situation
Step 1: Design mechanical action in fire
Design load in fire situation
Gk,j + 2,1 Qk,1 +  2,i Qk,i
j  1
i  2
Efi,d,t =
Self weight of the column
Total concentrated axial load from steel beams
secondary beam
main beam

## Slide 42: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Step 1: Design mechanical action in fire
Total design loading conditions in fire situation
1870.8 kN
Buckling length in fire situation
  pinned column base

## Slide 43: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Step 2: Classify member
Bending member
Web class 1
Flange class 1
Section
class 1
= 18.9
= 6.2
= 25.9
= 7.07
Table 5.2 of Eurocode 3 part 1-1
Relation 4.2 of Eurocode 3 part 1-2
Compression
S275
-
HEB300

## Slide 44: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Step 3: Design resistance at instant 0 (ambient temperature)
Design resistance at instant 0 (ambient temperature) according to Eurocode 3 part 1-2
Plastic axial resistance
Non-dimensional slenderness
HEB300 | 
A (cm²) | 149.08
Iz (cm) | 7.58

## Slide 45: 7.5. Example 5 : Buckling resistance of a column
7. Worked examples
Step 4: Degree of utilisation for tabulated data
Step 5: Critical temperature
linear interpolation of tabulated data
0.0
0.2
0.4
0.6
0.8
1.0
1.2
1.4
1.6
1.8
2.0
0
…
…
…
…
…
…
…
…
0.40
629
603
578
544
499
0.42
621
595
569
535
477
0.44
613
588
561
525
455
0.46
604
581
553
516
433
0.48
597
573
545
506
411
0.50
590
566
536
494
367
0.52
584
559
528
477
…
…
…
…